## Pipework
Name | Size (DN) | Internal Diameter (mm) | Colebrook White Coefficient | Safe Working Pressure (kPa) | Dynamic Viscosity (Ns/m2) @ 10degC | Dynamic Viscosity (Ns/m2) @ 15degC | Dynamic Viscosity (Ns/m2) @ 18degC | Dynamic Viscosity (Ns/m2) @ 20degC | Dynamic Viscosity (Ns/m2) @ 25degC | Dynamic Viscosity (Ns/m2) @ 38degC | Dynamic Viscosity (Ns/m2) @ 40degC | Dynamic Viscosity (Ns/m2) @ 43degC | Dynamic Viscosity (Ns/m2) @ 45degC | Dynamic Viscosity (Ns/m2) @ 50degC | Dynamic Viscosity (Ns/m2) @ 60degC | Dynamic Viscosity (Ns/m2) @ 65degC | Dynamic Viscosity (Ns/m2) @ 70degC | Fluid Density (kg/m3) | Commissioning + Testing | Maintenance
Copper (Type B) | 15 | 10.81 | 0.00015 | 5290 | 0.0013076 | 0.0011373 | 0.0010518 | 0.001 | 0.0008891 | 0.0006791 | 0.0006539 | 0.0006188 | 0.000597 | 0.0005474 | 0.0004656 | 0.000432 | 0.0004024 | 997 | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -Pipe supports installed as per relevant standard to the pipe material and also manufacturers details including seismic restraints -Pipe sizes are as per the design drawings -Pipe materials are as per the design drawings -Pipe runs have been marked out as per the design drawings and installed at the correct height -Dead leg capacity is compliant with the relevant standards and guidelines -Pipework identification installed at compliant distances -All openings in pipelines have been covered (and sealed with watertight plugs where applicable) to prevent contamination during construction -Proximity to other servicee is compliant with all relevant standards -The pipework has been installed in compliance with the manufacturers guidelines -Insulation has been installed as prescribed for acoustic and thermal insulation reasons as per the project requirements -Water services 80mm+ have been chlorinated in accordance with ANSI/AWWA C651 -The complete system has operated under normal working conditions for a period of at least 48 hours and there has been no visual leaks -All air has been fully purged from the system We would like to witness: -Flush the system at a minimum velocity of 0.75m/sec until the water runs completely clear prior to testing -Undertake a 1500kPa hydrostatic test for 30min with no leaks. Some fixtures cannot handle 1500KPA, these fixtures are to be disconnected for the 1500kPa test then reconnected and tested at their maximum operation pressure for 30min | Annual: -Inspect the visible pipework to ensure no leaks or potential issues -Ensure there is no undue noise from the system -Ensure the insulation is still wrapped as required
| 20 | 16.9 |  | 3970
| 25 | 22.8 |  | 3500
| 32 | 29.1 |  | 2780
| 40 | 35.4 |  | 2300
| 50 | 48.3 |  | 1710
| 65 | 61 |  | 1370
| 80 | 72.9 |  | 1520
| 100 | 98.2 |  | 1200
| 150 | 148.2 |  | 1000
| 200 | 198.9 |  | 720
HDPE (SDR11) | 16 | 12.65 | 0.0015 | 1600
| 20 | 16.05 |  | 1600
| 25 | 20.15 |  | 1600
| 32 | 25.95 |  | 1600
| 40 | 32.3 |  | 1600
| 50 | 40.4 |  | 1600
| 63 | 51 |  | 1600
| 75 | 61 |  | 1600
| 110 | 89.4 |  | 1600
| 160 | 130 |  | 1600
| 200 | 162.5 |  | 1600
| 225 | 182.9 |  | 1600
| 315 | 256.3 |  | 1600
PEX (SDR 7.4) | 16 | 11.35 | 0.0015 | 2500
| 20 | 14.15 |  | 2500
| 25 | 17.65 |  | 2500
| 32 | 22.75 |  | 2500
| 40 | 28.5 |  | 2500
| 50 | 35.7 |  | 2500
| 63 | 45.1 |  | 2500
| 75 | 53.6 |  | 2500
| 110 | 78.6 |  | 2500
| 160 | 114.7 |  | 2500
GMS (Medium) | 80 | 80.7 | 0.15 | 6530
| 100 | 105 |  | 5680
| 150 | 155 |  | 4330
Stainless Steel | 15 | 13 | 0.0015 | 20000
| 20 | 19.6 |  | 15800
| 25 | 25.6 |  | 12500
| 32 | 32 |  | 9800
| 40 | 39 |  | 8500
| 50 | 51 |  | 6800
| 65 | 72.1 |  | 7200
| 80 | 87.6 |  | 5900
| 100 | 104 |  | 4500
| 150 | 158 |  | 4000
Cast Iron (Coated) | 100 | 102 | 0.3 | 3500
| 150 | 157 |  | 3500
| 200 | 212 |  | 3500
| 225 | 238.6 |  | 3500
| 250 | 264.8 |  | 3500
| 300 | 322.4 |  | 3500
Add new pipe

## Insulation
Name | Water Temp (degC) | Ambient Temp (degC) | Size (DN) | U Value
Standard
25mm Insulation | 65 | 20 | 15 | 6.7
|  |  | 20 | 7.5
|  |  | 25 | 9.8
|  |  | 32 | 10.5
|  |  | 40 | 12.1
|  |  | 50 | 14.5
|  |  | 65 | 16.2
|  |  | 80 | 19.1
|  |  | 100 | 22.9
|  |  | 150 | 28.7
38mm Insulation | 65 | 20 | 15 | 4.75
|  |  | 20 | 5.621
|  |  | 25 | 6.574
|  |  | 32 | 7.309
|  |  | 40 | 8.273
|  |  | 50 | 9.864
|  |  | 65 | 11.413
|  |  | 80 | 12.911
|  |  | 100 | 15.921
|  |  | 150 | 21.815
25mm Insulation | 43 | 20 | 15 | 3.73
|  |  | 20 | 4.64
|  |  | 25 | 5.48
|  |  | 32 | 6.29
|  |  | 40 | 7.07
|  |  | 50 | 8.62
|  |  | 65 | 10.13
|  |  | 80 | 11.62
|  |  | 100 | 14.57
|  |  | 150 | 20.32
Add a new insulation

## Valves + Fittings
Name | Abbreviation | Symbol | Size (DN) | K Value | Commissioning + Testing | Maintenance
Gate Valve | GV |  | 15 | 0.22 | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -All valves have been checked to confirm their correct performance | Annual: -Inspect the visible valves to ensure no leaks or potential issues -Ensure the isolation valves are correctly in the open or closed position
|  |  | 20 | 0.2
|  |  | 25 | 0.18
|  |  | 32 | 0.18
|  |  | 40 | 0.17
|  |  | 50 | 0.15
|  |  | 65-80 | 0.14
|  |  | 100 | 0.14
|  |  | 150 | 0.12
|  |  | 200-250 | 0.11
|  |  | 315 | 0.1
Ball Valve | BV |  | 15 | 0.08
|  |  | 20 | 0.08
|  |  | 25 | 0.07
|  |  | 32 | 0.07
|  |  | 40 | 0.06
|  |  | 50 | 0.06
|  |  | 65-80 | 0.05
|  |  | 100 | 0.05
|  |  | 150 | 0.05
|  |  | 200-250 | 0.04
|  |  | 315 | 0.04
Butterfly Valve | BFV |  | 50 | 0.86
|  |  | 65-80 | 0.81
|  |  | 100 | 0.77
|  |  | 150 | 0.68
|  |  | 200-250 | 0.56
|  |  | 315 | 0.39
90 Elbow | NA | NA | 15 | 0.81
|  |  | 20 | 0.75
|  |  | 25 | 0.69
|  |  | 32 | 0.66
|  |  | 40 | 0.63
|  |  | 50 | 0.57
|  |  | 65-80 | 0.54
|  |  | 100 | 0.51
|  |  | 150 | 0.45
|  |  | 200-250 | 0.42
|  |  | 315 | 0.39
45 Elbow | NA | NA | 15 | 0.43
|  |  | 20 | 0.4
|  |  | 25 | 0.37
|  |  | 32 | 0.35
|  |  | 40 | 0.34
|  |  | 50 | 0.3
|  |  | 65-80 | 0.29
|  |  | 100 | 0.27
|  |  | 150 | 0.24
|  |  | 200-250 | 0.22
|  |  | 315 | 0.21
Check Valve | CV |  | 15 | 2.7
|  |  | 20 | 2.5
|  |  | 25 | 2.3
|  |  | 32 | 2.2
|  |  | 40 | 2.1
|  |  | 50 | 1.9
|  |  | 65-80 | 1.8
|  |  | 100 | 1.7
|  |  | 150 | 1.5
|  |  | 200-250 | 1.4
|  |  | 315 | 1.3
T - Thru Flow | NA | NA | 15 | 0.54
|  |  | 20 | 0.5
|  |  | 25 | 0.46
|  |  | 32 | 0.44
|  |  | 40 | 0.42
|  |  | 50 | 0.38
|  |  | 65-80 | 0.36
|  |  | 100 | 0.34
|  |  | 150 | 0.3
|  |  | 200-250 | 0.28
|  |  | 315 | 0.26
T - Thru Branch | NA | NA | 15 | 1.62
|  |  | 20 | 1.5
|  |  | 25 | 1.38
|  |  | 32 | 1.32
|  |  | 40 | 1.26
|  |  | 50 | 1.14
|  |  | 65-80 | 1.08
|  |  | 100 | 1.02
|  |  | 150 | 0.9
|  |  | 200-250 | 0.84
|  |  | 315 | 0.78
Water Meter | WM |  | All | 7
Strainer | ST |  | All | 2
Change in Pipe Size | NA | NA | 0.8*(sin(Ø/2))*()1-(diameter of large pipe^2/diameter of smaller pipe^2)

## Fixtures
Name | LU AS3500 |  | LU (Other) |  | Q (l/s) |  | FU | Warm Temp. (degC) | Outlet Above Floor (m) | Template Roughin Layout | Min. Inlet Pressure (kPa) | Max. Inlet Pressure (kPa) | Commissioning + Testing | Maintenance
| Cold | Hot | Cold | Hot | Cold | Hot
Basin | 1 | 1 | 1 | 1 | 0.1 | 0.1 | 1 | 42 | 1 |  | 200 | 500 | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -All fixtures have been checked to confirm their correct performance -Tapware and basin have been installed at the correct setout as per the architectural room layout sheets -Tapware and basins installed have been approved by the client We would like to witness: -The flow rate of the fixtures verified against the architectural specification | Annual: -Ensure the flow rate and pressure at the fixture is in line with the architectural specification -Ensure the drain is free flowing and there are no gurgling noises in the system
Shower | 2 | 2 | 3 | 2 | 0.1 | 0.1 | 2 | 42 | 1.5 |  | 200 | 500
WC | 2 | 0 | 2 | 0 | 0.1 | 0 | 4 | NA | 0.75 |  | 200 | 500
Bath | 8 | 4 | 8 | 8 | 0.3 | 0.3 | 4 | 42 | 0.75 |  | 200 | 500
Kitchen sink | 2 | 2 | 2 | 3 | 0.1 | 0.2 | 3 | NA | 1 |  | 200 | 500
Washing Machine | 3 | 2 | 3 | 3 | 0.2 | 0.2 | 5 | NA | 0.8 |  | 200 | 500
Dishwasher | 3 | 2 | 3 | 3 | 0.2 | 0.2 | 3 | NA | 0.8 |  | 200 | 500
Laundry Trough | 3 | 3 | 3 | 3 | 0.12 | 0.2 | 4 | NA | 1 |  | 200 | 500
Ensuite (WC, Basin & Shower) | 5 | 3 | 5 | 3 | 0.3 | 0.2 | 6 | NA | NA |  | 200 | 500
Dual Ensuite (2 x WC, 2 x Basin & 2 x Shower) | 10 | 6 | 10 | 6 | 0.6 | 0.4 | 12 | NA | NA |  | 200 | 500
Beverage Bay | 2 | 2 | 2 | 2 | 0.1 | 0.1 | 1 | 42 | 1 |  | 200 | 500
WC + Basin | 3 | 1 | 3 | 1 | 0.2 | 0.1 | 5 | NA | NA |  | 200 | 500
Ensuite (WC, Basin & Shower) + Basin | 6 | 4 | 6 | 4 | 0.4 | 0.3 | 7 | NA | NA |  | 200 | 500
Dual Ensuite (2 x WC, 2 x Basin & 2 x Shower) + 2 x Basin | 12 | 8 | 12 | 8 | 0.8 | 0.6 | 14 | NA | NA |  | 200 | 500
Scrub Trough | ? | ? | ? | ? | 0.45 | 0.45 | ? | 42 | 1 |  | 200 | 500
Urinal | ? | ? | ? | ? | 0.5 | 0 | 2 | NA | NA |  | 200 | 500
Birthing Pool | ? | ? | ? | ? | 1 | 1 | 22 | 38 | 0.75 |  | 200 | 500
Flishing Rim Sink | ? | ? | ? | ? | ? | ? | ? | NA | 1 |  | 200 | 500
Sanitiser | ? | ? | ? | ? | ? | ? | ? | NA | 1 |  | 200 | 500
Dirty Utility ( Sink, Basin, Sanitiser, Flushing Rim Sink) | ? | ? | ? | ? | ? | ? | 13 | NA | NA |  | 200 | 500
Cleaners sink | 2 | 2 | 2 | 3 | 0.12 | 0.2 | 1 | NA | 1 |  | 200 | 500
Apartment (basin,shower, bath, WC, Kitchen Sink, Laundry Trough, Washing Machine) | 21 | 14 | 22 | 20 | 1.02 | 1.1 | 18 | NA | NA |  | 200 | 500
Continuous Flow | Specified in the properties each time (this is added to the PSD and is not diversified)
Add a new fixture

## Backflow Valves
Name | Size | Min. Inlet Pressure (kPa) | Max. Inlet Pressure (kPa) | Minimum Flow Rate (L/s) | Maximum Flow Rate (L/s) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Commissioning | Maintenance
Standard
RPZD | 15 | 200 | 2000 | 0 | 0.48 | 60 @ 0.05 L/sec | 90 @ 0.17 L/sec | 85 @ 0.37 L/sec | 80 @ 0.48 L/sec | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -The location of the RPZD has been installed as per the design drawings and architectural requirements -The RPZD is accessible for maintenance -The RPZD has been installed as per the manufacturers guidelines We would like to witness: -The discharge of the RPZD does not overflow -The non-potable fixtures downstream of the RPZD have no flow when the RPZD is isolated -The fixtures used for personal hygiene still operate when the local RPZD is isolated -Test the RPZD pressure differential -Stickers indicating 'Not for Drinking' installed at each outlet | Annually: -To be tested as per the manufacturers requirements to ensure working order
| 20 | 200 | 2000 | 0.49 | 0.83 | 75 @ 0.49 L/sec | 70 @ 0.6 L/sec | 73 @ 0.7 L/sec | 74 @ 0.83 L/sec
| 25 | 200 | 2000 | 0.84 | 1.36 | 67 @ 0.84 L/sec | 65 @ 1 L/sec | 64 @ 1.2 L/sec | 65 @ 1.36 L/sec
| 32 | 200 | 2000 | 1.37 | 2.3 | 82 @ 1.37 L/sec | 75 @ 1.7 L/sec | 70 @ 2 L/sec | 68 @ 2.3 L/sec
| 40 | 200 | 2000 | 2.31 | 3.25 | 87 @ 2.31 L/sec | 85 @ 2.6 L/sec | 85 @ 2.9 L/sec | 85 @ 3.25 L/sec
| 50 | 200 | 2000 | 3.26 | 5.15 | 87 @ 3.26 L/sec | 85 @ 4 L/sec | 85 @ 4.5 L/sec | 85 @ 5.15 L/sec
| 65 | 200 | 2000 | 5.16 | 7.5 | 97 @ 5.16 L/sec | 97 @ 6 L/sec | 98 @ 7 L/sec | 97 @ 7.5 L/sec
| 80 | 200 | 2000 | 7.51 | 12 | 85 @ 7.51 L/sec | 85 @ 9 L/sec | 87 @ 11 L/sec | 88 @ 12 L/sec
| 100 | 200 | 2000 | 12.01 | 20 | 67 @ 12.01 L/sec | 65 @ 15 L/sec | 65 @ 18 L/sec | 65 @ 20 L/sec
| 150 | 200 | 2000 | 20.01 | 45 | 74 @ 20.01 L/sec | 74 @ 28 L/sec | 74 @ 36 L/sec | 75 @ 45 L/sec
| X | 200 | 2000 | 0.001 | 999 | 70kPa
Add a new backflow valve

## Mixing Valves
Name | Min. Inlet Pressure (kPa) | Max. Inlet Pressure (kPa) | Max. Hot and Cold Pressure Differential | Minimum Flow Rate (L/s) | Maximum Flow Rate (L/s) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Pressure Loss @ Flow Rate (kPa) | Commissioning + Testing | Maintenance | BMCS
Standard
TMV | 20 | 500 | 10% | 0.066 | 0.65 | 30kPa @ 0.16 L/sec | 80kPa @ 0.32 L/sec | 160kPa @ 0.48 L/sec | 300kPa @ 0.65 L/sec | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -The temperature of the TMV has been set -The location of the TMV has been installed as per the design drawings and architectural requirements -The TMV is accessible for maintenance -The TMV has been installed as per the manufacturers guidelines We would like to witness: -The outlet temperature is in accordance with the required temperature -The thermal shutdown of the TMV when the cold water supply is isolated | Annual: -To be cleaned including the strainer -Ensure the outlet temperature is correct -Undertake a thermal shutdown -Check the non return valve operation Every five years: -Replace the body of the valve including the 'O' ring and thermostatic element | Anologue output - TMV hubs to monitor temperature
Tempering Valve | 20 | 500 | 10% | 0.066 | 0.6 | 3kPa @ 0.08L/sec | 12kPa @ 0.16 L/sec | 50kPa @ 0.32 L/sec | 150kPa @ 0.6 L/sec | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -The tempering valve is accessible for maintenance -The tempering valve has been installed as per the manufacturers guidelines We would like to witness: -The outlet temperature is in accordance with the required temperature | Annual: -Ensure the outlet temperature is correct | NA
Add a new mixing valve

## PRV
Name | Size | Min. Inlet Pressure (kPa) | Max. Inlet Pressure (kPa) | Minimum Flow Rate (L/s) | Max. Pressure Drop Ratio | Maximum Flow Rate (L/s) | Commissioning + Testing | Maintenance
Standard
PRV 1 | 15 | 200 | 2000 | 0.25 | 2 to 1 | 0.5 | Provide ITPs for review that show the following have been undertaken to allow the compliant installation wth quality workmanship: -The pressure reduction valve has been installed in line with the manufacturers guidelines We would like to witness: -The pressure at the most advantaged point of the system during a peak and non peak demand -The pressure at the most disadvantaged point of the system during a peak and non peak demand -The pressure on each level of the building during peak and non peak demand -That there is no noise caused by the pressure reduction valve during peak and non peak demand | Annual: -Check the pressure at each level of the building matches the design intent
| 20 | 200 | 2000 | 0.51 | 2 to 1 | 0.83
| 25 | 200 | 2000 | 0.84 | 2 to 1 | 1.33
| 32 | 200 | 2000 | 1.34 | 2 to 1 | 2.33
| 40 | 200 | 2000 | 2.34 | 2 to 1 | 3
| 50 | 200 | 2000 | 3.01 | 2 to 1 | 4
| 65 | 200 | 2000 | 4.01 | 2 to 1 | 5.7
| 80 | 200 | 2000 | 5.71 | 2 to 1 | 8.5
| 100 | 200 | 2000 | 8.51 | 2 to 1 | 15
| 150 | 200 | 2000 | 15.01 | 2 to 1 | 34
Add a new PRV

## Budget
Item | Unit of Measurement | Cost / Unit ($)
x | x | x

## PSD
DIN | Barrie's Book - LU | Barrie's Book - Dwellings | AS3500.1 LU